## OUTPUT
Project: | [5 empty] | Rep: |  | Engr.:
Item | TAG (Location) | Duct Size (in) |  | Pressure | Immediate Up/Downstream Disturbances | [7 empty] | Z | Locate Probes |  |  | Source | Inst. ACC ± | Diagram
[5 empty] | Upstream |  | Downstream | [6 empty] | Opt. | Range
|  | Width | Height |  | Description | Fig. | Description | Fig. | Xmin | Xcalc | Ymin | Ycalc |  | L | X | Y

## Table_A-1_Data_Pos_Up (hidden)
RELATIONSHIP TO FAN → | POSITIVE
Upstream
| Figure | X
|  | Xmin | Xcalc
Disturbance ↓
Air Cleaners - Filter (pleated) | A-X-01 | 24
Air Cleaners - Filter (roll) | A-X-02 | 12
Coils and Heaters - H/W Coil | C-X-01 | 18
Coils and Heaters - C/W Coil | C-X-01 | 18
Dampers - Ducted (2-position, Open/Closed) | D-X-01 | 20
Elbow (no turning vanes) | E-X-01 | 36 | 3
Elbow (turning vanes) | E-X-02 | 9 | 0.75
Elbow (radius or sweep) | E-X-03 | 21 | 1.75
Fans (Ducted) - Centrifugal | F-X-01 | 24 | 2
Fans (Ducted) - Vane Axial | F-X-02 | 24 | 2
Fan Plenums - Plenum to Duct | P-X-01 | 18 | 1.5
T Main Duct (no turning vanes) | T-X-01 | 12 | 1
T Main Duct (turning vanes) | T-X-03 | 18 | 1.5
T Branch Duct (no turning vanes) | T-X-05 | 36 | 3
T Branch Duct (turning vanes) | T-X-06 | 18 | 1.5
Terminal T (no turning vanes) | T-X-07 | 36 | 3
Terminal T (turning vanes) | T-X-08 | 18 | 1.5
Reducing Transition | Z-X-01 | 6 | 0.5
Expanding Transition | Z-X-02 | 18 | 1.5

## Table_A-1_Data_Pos_Down (hidden)
RELATIONSHIP TO FAN → | POSITIVE
Downstream
| Figure | Y
|  | Ymin | Ycalc
Disturbance ↓
Air Cleaners - Filter (pleated) | A-Y-01 | 6
Air Cleaners - Filter (roll) | A-Y-02 | 6
Coils and Heaters - H/W Coil | C-Y-01 | 6
Coils and Heaters - C/W Coil | C-Y-01 | 6
Dampers - Ducted (Modulating) | D-Y-01 | 9 | 0.75
Dampers - Ducted (2-position, Open/Closed) | D-Y-01 | 10
Elbow (no turning vanes) | E-Y-01 | 18 | 1.5
Elbow (turning vanes) | E-Y-02 | 9 | 0.75
Elbow (radius or sweep) | E-Y-03 | 21 | 1.75
Exhaust Louvers - Backdraft | L-Y-01 | 30
Exhaust Louvers - Stationary | L-Y-01 | 18
T Main Duct (no turning vanes) | T-Y-01 | 6 | 0.5
T Main Duct (turning vanes) | T-Y-03 | 6 | 0.5
Terminal T (no turning vanes) | T-Y-07 | 12 | 1
Terminal T (turning vanes) | T-Y-08 | 9 | 0.75
Reducing Transition | Z-Y-01 | 6 | 0.5
Expanding Transition | Z-Y-02 | 6 | 0.5

## Table_A-1_Data_Neg_Up (hidden)
RELATIONSHIP TO FAN → | NEGATIVE
Upstream
| Figure | X
|  | Xmin | Xcalc
Disturbance ↓
Air Cleaners - Filter (pleated) | A-X-01 | 18
Air Cleaners - Filter (roll) | A-X-02 | 12
Coils and Heaters - H/W Coil | C-X-01 | 18
Coils and Heaters - C/W Coil | C-X-01 | 18
Dampers - Ducted (2-position, Open/Closed) | D-X-01 | 20
Elbow (no turning vanes) | E-X-01 | 36 | 3
Elbow (turning vanes) | E-X-02 | 9 | 0.75
Elbow (radius or sweep) | E-X-03 | 21 | 1.75
OA Intake - Angled (or Radiused) Hoods | H-X-01 | 12
OA Intake - Straight Through Hoods | H-X-02 | 12
OA Intake - Hurricane/Rain Louvers <500 FPM | L-X-01 | 18
OA Intake - Hurricane/Rain Louvers 500 to 1,250 FPM | L-X-01 | 24
OA Intake - Hurricane/Rain Louvers >1,250 FPM | L-X-01 | 36
OA Intake - Stationary Louvers < 6 in. <500 FPM | L-X-01 | 18
OA Intake - Stationary Louvers < 6 in. 500 to 1,250 FPM | L-X-01 | 24
OA Intake - Stationary Louvers < 6 in. >1,250 FPM | L-X-01 | 36
OA Intake - Stationary Louvers ≥ 6 in. <500 FPM | L-X-01 | 12
OA Intake - Stationary Louvers ≥ 6 in. 500 to 1,250 FPM | L-X-01 | 18
OA Intake - Stationary Louvers ≥ 6 in. >1,250 FPM | L-X-01 | 24
Outdoor Air Intake Plenum to Duct <500 FPM | P-X-01 | 6
Outdoor Air Intake Plenum to Duct 500 to 1,250 FPM | P-X-01 | 12
Outdoor Air Intake Plenum to Duct >1,250 FPM | P-X-01 | 18
T Main Duct (no turning vanes) | T-X-02 | 18 | 1.5
T Main Duct (turning vanes) | T-X-04 | 12 | 1
Terminal T (no turning vanes) | T-X-07 | 24 | 2
Terminal T (turning vanes) | T-X-08 | 12 | 1
Reducing Transition | Z-X-01 | 6 | 0.5
Expanding Transition | Z-X-02 | 18 | 1.5

## Table_A-1_Data_Neg_Down (hidden)
RELATIONSHIP TO FAN → | NEGATIVE
Downstream
| Figure | Y
|  | Ymin | Ycalc
Disturbance ↓
Air Cleaners - Filter (pleated) | A-Y-01 | 6
Air Cleaners - Filter (roll) | A-Y-02 | 6
Coils and Heaters - H/W Coil | C-Y-01 | 6
Coils and Heaters - C/W Coil | C-Y-01 | 6
Dampers - Ducted (Modulating) | D-Y-01 | 9 | 0.75
Dampers - Ducted (2-position, Open/Closed) | D-Y-01 | 10
Dampers - OA Intake 4 in. Blade ≤1,250 FPM | D-Y-01 | 4
Dampers - OA Intake 6 in. Blade ≤1,250 FPM | D-Y-01 | 6
Dampers - OA Intake 8 in. Blade ≤1,250 FPM | D-Y-01 | 8
Elbow (no turning vanes) | E-Y-01 | 18 | 1.5
Elbow (turning vanes) | E-Y-02 | 9 | 0.75
Elbow (radius or sweep) | E-Y-03 | 21 | 1.75
Fans (Ducted) - Centrifugal | F-Y-01 | 12 | 1
Fans (Ducted) - Vane Axial | F-Y-02 | 12 | 1
Fan Plenums - Duct to Plenum | P-Y-01 | 12 | 1
T Main Duct (no turning vanes) | T-Y-02 | 6 | 0.5
T Main Duct (turning vanes) | T-Y-04 | 6 | 0.5
T Branch Duct (no turning vanes) | T-Y-05 | 12 | 1
T Branch Duct (turning vanes) | T-Y-06 | 12 | 1
Terminal T (no turning vanes) | T-Y-07 | 6 | 0.5
Terminal T (turning vanes) | T-Y-08 | 6 | 0.5
Reducing Transition | Z-Y-01 | 6 | 0.5
Expanding Transition | Z-Y-02 | 6 | 0.5